## Wire to Water Energy Calculator
Wire to Water Energy Calculator
| REQUIRED DATA | PUMP 1 |  |  | PUMP 2
| Pump Operation - Hours / Day | 8 |  |  | 8
| Pump Operation - Days / Year | 365 |  |  | 365
| Pump Flow - GPM | 300 |  |  | 300
| Pump Head - Feet | 90 |  |  | 90
| Pump Efficiency - % | 75% |  |  | 62%
| Motor Efficiency - % | 90% |  |  | 90%
| Energy Cost in $/KWH | 0.1 |  |  | 0.1
| Specific Gravity of fluid | 1.2 |  |  | 1.2
RESULTS
| BHP At Design Point | 10.9091 |  |  | 13.1965
| Wire to Water Efficiency - % | 67.5% |  |  | 55.8%
| Annual Energy Cost | 2640.3879 | 9.0424 | 10.9384 | 3194.0176
| KW Per 1000 Gallons Pumped | 0.50236 | 3.3333 | 3.3333 | 0.60769
| Cost Per 1000 Gallons Pumped | 0.050236 |  |  | 0.060769
PAYBACK
| Annual Savings - $$ | 553.6297 |  |  | Note: When comparing two pumps, place the lower efficiency pump/motor in the Pump 2 row.
| Annual Savings - % | 17.33%
| Cost of Pump 1 | 7000
| Cost of Pump 2 | 5000
| Payback - Years | 3.6125